## Sheet1
Ashuganj Power Station Company Limited 400MW CCPP East Updated: 03.11.2022
SL NO. | Date | Time Out/In | Unit GT/ST | Start/ S/D/Trip | Cause | Maintenance Work done
1 | 29.05.22 | 13:22 | GT | First time fired | GT speed up to 33.178 hz
2 | 30.05.22 | 10:39 | GT | 2nd time fired | GT speed up to 50 hz
3 | 30.05.22 | 11:09 | GT | shutdown | Press Emergency PB
4 | 18.06.22 | 10:00 | GT | Speed up to 50hz | Excitation test going on
5 | 18.06.22 | 16:54 | GT | Tripped | Due to Overspeed trip protection
7 | 20.06.22 | 12:42 | GT | Synchronized
8 | 20.06.22 | 12:45 | GT | Tripped | Due to HCO state monitoring GT tripped
9 | 20.06.22 | 15:48 | GT | Synchronized
10 | 20.06.22 | 16:09 | GT | shutdown | As per SIEMENS requirement
11 | 21.06.22 | 9:11 | GT | Synchronized
12 | 21.06.22 | 16:28 | GT | shutdown | Partial Load Tuning test done.
13 | 22.06.22 | 9:34 | GT | Synchronized
14 | 22.06.22 | 16:14 | GT | shutdown | Partial Load Tuning test done.
15 | 23.06.22 | 9:11 | GT | Synchronized
16 | 23.06.22 | 16:00 | GT | shutdown | Load Tuning test complited.
17 | 24.06.22 | 9:31 | GT | Synchronized
18 | 24.06.22 | 16:58 | GT | shutdown | Compressor casing vibration protection test
20 | 25.06.22 | 10:01 | GT | Synchronized
21 | 25.06.22 | 17:10 | GT | shutdown | Normal shutdown.
22 | 27.06.22 | 9:49 | GT | Synchronized
23 | 27.06.22 | 10:07 | GT | shutdown | Due to low gas pressure.
24 | 27.06.22 to 29.06.22 |  |  |  | Not Started due to low gas pressure.
25 | 30.06.22 | 8:28 | GT | Synchronized
26 | 30.06.22 | 17:10 | GT | shutdown | Normal shutdown.
27 | 02.07.22 | 8:40 | GT | Synchronized
28 | 02.07.22 | 16:31 | GT | shutdown | Load rejection test 50% complited
29 | 04.07.22 | 9:23 | GT | Synchronized
30 | 04.07.22 | 9:32 | GT | Tripped | Due to acceleration monitoring > Max3
31 | 06.07.22 | 6:50 | GT | Synchronized
32 | 06.07.22 | 14:45 | GT | shutdown | Emission test complited
33 | 07.07.22 |  |  |  | Not Started due to low gas pressure.
34 | 08.07.22 | 7:14 | GT | Synchronized | Frequency response test going on.
35 | 08.07.22 | 16:27 | GT | Tripped | GT tripped due to low gas pressure at the time of 100% load rejection test
36 | 09.07.22 | 7:12 | GT | Synchronized
37 | 09.07.22 | 16:36 | GT | Shutdown | Excitation test going on.
38 | 10.07.22 |  |  |  | NLDC not given permission due to EID day.
39 | 11.07.22 | 7:12 | GT | Synchronized
40 | 11.07.22 | 14:26 | GT | Shutdown | Excitation test complited
41 | 12.07.22 | 7:17 | GT | Synchronized | Unit ckt breaker switching (house load) test
42 | 12.07.22 | 14:22 | GT | Tripped | Due to fire protection Aux. group-1
43 | 13.07.22 | 10:28 | GT | FSNL | Steam blowing
44 | 13.07.22 | 16:41 | GT | Shutdown | Due to demi water shortage
45 | 14.07.22 | 10:31 | GT | Synchronized | Steam blowing
46 | 14.07.22 | 19:45 | GT | Shutdown | Due to demi water shortage
47 | 15.07.22 | 8:36 | GT | FSNL | Steam blowing
48 | 15.07.22 | 22:58 | GT | Damper closed but GT running at FSNL | Steam blowing stopped due to demi water shortage but GT runing condtion at FSNL up to 08:04 AM dated 16/07/22
49 | 16.07.22 | 10:35 | GT | Shutdown | Due to HP temporary pipe line leakage
50 | 18.07.22 | 10:58 | GT | FSNL | After repairing the leakage & Steam blowing started.
51 | 18.07.22 | 15:30 | GT | Shutdown | Due to HP temporary pipe line leakage
52 | 19.07.22 to 21.07.22 |  |  |  | Not Started due to low gas pressure.
53 | 22.07.22 | 6:04 | GT | FSNL | For Steam Blowing
54 | 22.07.23 | 10:06 | GT | Shutdown | Due to gas shortage.
55 | 23.07.22 to 28.07.22 |  | GT |  | Not Started due to low gas pressure.
56 | 29.07.22 | 5:51 | GT | FSNL | For Steam Blowing
57 | 29.07.23 | 19:37 | GT | Synchronized
58 | 29.07.24 | 23:39 | GT | Shutdown | After cpmplete steam blowing
59 | 30.07.22 to 16.09.2022 |  |  |  | Comissioning work by CNTIC
60 | 17.09.2022 | 13:48 | GT | Synchronized | GT running with 13 MW and waiting for steam quality.
61 | 17.09.2022 | 16:05 | GT | GCB Open | GT running with FSNL and waiting for steam quality.
62 | 21.09.2022 to 26.09.2022 | 12:06 | GT | Synchronized | GT running with 13 MW and waiting for steam quality.
63 | 27.09.2022 | 9:05 | ST | ST started | Steam admitted to steam turbine and at 600 RPM condition fulfill for next step.
64 | 27.09.2023 | 9:41 | ST |  | ST given shutdown by SIEMENS manually at ST speed 2250 RPM..
65 | 27.09.2024 | 11:07 | ST | ST Engaged | ST again started and succesfully engaged with GT.
66 | 27.09.2022 | 16:52 | ST | ST Shutdown | ST given shutdown by SIEMENS at combined cycle load 130 MW.
67 | 28.09.2022 | 10:03 | ST | ST Engaged
68 | 28.09.2022 | 13:11 | ST | ST Shutdown | Due to HP control valve support spring locked.
69 | 28.09.2023 | 17:20 | GT | Shutdown | Due to HP control valve support spring locked and lifting oil system leakage.
70 | 29.09.2022 to 03.10.2022 |  | GT | Shutdown | Due to HP control valve support spring locked remove and lifting oil system leakage repair work.
71 | 04.10.2022 | Night | GT |  | Tried to start several times by CNTIC but failed due to SFC blocked alarm
72 | 04.10.2022 | 11:31 | GT | GT FSNL
73 | 04.10.2022 | 14:04 | GT | GT tripped | Due to National Grid problem
74 | 05.10.2022 | 11:19 | GT | Synchronized
75 | 05.10.2022 | 17:34 | GT | Tripped | Due to turbine outlet temp. burn monitoring on (Hot spot). Turbine outlet temp. sensor no:11 was faulty.
76 | 05.10.2022 | 19:20 | GT | Synchronized | GT running with 13 MW and waiting for steam quality.
77 | 06.10.2022 | 15:13 | ST | ST started | Steam admitted to steam turbine and at 600 RPM waiting for condition fulfill to go next step.
78 | 06.10.2022 | 17:10 | ST | ST Shutdown | Due to steam quality not came within the range as per SIEMENS requirment.
79 | 07.10.2022 | 8:30 | ST | ST Engaged
80 | 07.10.2022 | 9:12 | ST | ST tripped | Due to seal steam system fault.
81 | 07.10.2022 | 17:34 | GT | Tripped | Due to turbine outlet temp. burn monitoring on (Hot spot). Turbine outlet temp. sensor no:13 was faulty.
82 | 08.10.22 to 13.10.22 |  | GT & ST | Shutdown | BPDB not given permission to start the plant due to low gas pressure.
83 | 14.10.22 | 0:27 | GT | GT FSNL | GT running with FSNL, bypass open at 01:40 hrs and waiting for steam quality.
84 | 14.10.22 | 8:33 | GT | Synchronized | Running with 20MW and waiting for steam quality.
85 | 14.10.22 | 12:40 | ST | ST Engaged
86 | 14.10.22 | 14:56 | ST | Shutdown | Due to steam conductivity high but GT running for steam quality.
87 | 15.10.22 | 8:03 | ST | ST Engaged | at about 15:22 hrs combined cycle load reached at 435 MW.
88 | 15.10.22 | 17:06 | GT & ST | Tripped | Due to HP Steam temperature high.
89 | 15.10.22 | 18:00 | GT | GT FSNL | GT running with FSNL, bypass operation and waiting for steam quality.
90 | 16.10.22 | 8:55 | GT | Synchronized
91 | 16.10.22 | 9:00 | GT | Shutdown | Due to Turbine outlet temp. deviation high
92 | 16.10.22 | 10:11 | GT | Synchronized | Running with 20MW and waiting for steam quality.
93 | 16.10.22 | 11:03 | GT | Shutdown | Given shutdown for hot start tuning
94 | 16.10.22 | 12:58 | GT | Started | Started at 12:58 hrs but at 13:03 hrs tripped due to acceleration monitoring max>3 at the time of GT hot tuning.
95 | 16.10.22 | 16:34 | GT | Synchronized
96 | 16.10.22 | 17:51 | GT | Shutdown | Due to Turbine outlet temp. deviation high
97 | 17.10.22 | 21:18 | GT | Synchronized
98 | 18.10.22 | 8:02 | ST | ST Engaged | Combined cycle commissioning going on
99 | 18.10.22 to 21.10.22 |  |  |  | Combined cycle commissioning going on
100 | 21.10.22 | 11:52 |  |  | GBC-3 tripped and load reduced to 200MW automatically (50MW/Min)
101 | 21.10.22 | 12:44 |  |  | GBC-3 again started and load increased for commissioning
102 | 23.10.22 | 15:22 | ST |  | ST full load rejection test done succesfully
103 | 23.10.22 | 20:40 | ST | ST Engaged | Combined cycle commissioning going on
104 | 24.10.22 | 19:03 | ST | ST disengaged | After completting Combined cycle commissioning
105 | 24.1022 | 20:32 | GT | Shutdown
106 | 27.10.22 | 15:19 | GT | Synchronized | For performance test
107 | 28.10.22 | 13:56 | GT | Tripped | GT tripped from full load due to acceleration monitoring max>3 at the time of GT performance test.
108 | 29.10.22 to 14.11.22 |  |  |  | MI completed by Siemens | CC inspection by Siemens and spare parts provided by CNTIC (123 pcs tiles changed)
109 | 14.11.22 | 14:04 and 14:20 | GT and ST |  | Turning gear on.
110 | 14.11.22 | 22:03 | GT | Synchronized
111 | 15.11.22 | 12:56 | ST | ST Engaged
112 | 16.11.22 to 26.11.22 |  |  |  | RRT and COD completed.
113 | 29.11.22 | 1:09 | ST | ST Disengaged | For Performance test preparation
114 | 29.11.22 to 30.11.22 | 2:56 | GT | Shutdown
115 | 01.12.22 | 2:46 | GT | Synchronized | Performance test completed
| 02.12.2022 | 1:33 | ST | ST Engaged
116 | 01.12.22 to 7.12.22 | 15:40
| 06.12.22 | 9:06 | ST | ST Disengaged | For Performance test
|  | 11:03 | ST | ST Engaged
| 07.12.22 | 8:34 | ST | ST Disengaged | For GT hot start tuning
|  | 9:46 | ST | ST Engaged
117 | 08.12.22 | 14:28 | ST | ST Disengaged
118 | 08.12.22 | 14:58 | GT | Shutdown
119 | 08.12.22 | 15:43 | GT | Tripped | GT tripped during start-up due to acceleration monitoring max>3 at the time of hot start tuning.
120 | 10.12.22 | 22:55 | GT | Synchronized
121 | 11.12.22 | 6:57 | GT | Shutdown | For GT hot start tuning
122 | 11.12.22 | 7:56 | GT | Synchronized | GT hot start tuning successful
123 | 11.12.22 | 15:08 | ST | ST Engaged
124 | 11.12.22 to 31.12.22 |  | GT & ST |  | Plant running normal
125 | 02.01.23 | 10:47 | GT & ST | Tripped | Plant tripped due to 400 KV control power failure at 400KV GIS
126 |  | 15:37 | GT | Synchronized
127 |  | 20:11 | ST | ST Engaged
128 | 03.01.23 | 9:17 | GT & ST | Tripped | Plant tripped due to 400 KV control power failure at 400KV GIS
129 |  | 13:57 | GT | Synchronized
130 |  | 18:38 | ST | ST Engaged
131 | 17.01.23 | 11:42 | ST | ST Disengaged | Plant shutdown as per NLDC demand due to bad weather | Coalescer filter change
132 |  | 12:23 | GT | Shutdown
133 | 20.01.23 | 14:04 | GT | Synchronized
134 |  | 19:15 | ST | ST Engaged
135 | 10.02.23 | 9:04:00 AM & 09:27 | GT & ST | ST tripped and GT shutdown | ST Tripped at 09:04 hrs due to HRH TEMP PRD Trip and GT given shutdown at 09:27 hrs due to air intake filter DP high. | Fine filter change
136 |  | 21:20 | GT | Synchronized
137 | 11.02.23 | 11:04 | ST | ST Engaged
138 | 26.02.23 | 17:30 | ST | Tripped | ST Tripped at 17:30 hrs due to IP drum level fluctuation
139 |  | 21:37 | ST | ST Engaged
140 | 13.03.23 | 10:20 | GT & ST | Tripped | GT tripped at 10:20 hrs due to GT HW TRIP SYSTEM active
141 |  | 14:47 |  | Synchronized
142 |  | 20:02 |  | ST Engaged
143 | 24.03.23 | 14:28 | ST | Tripped | ST tripped at 14:28 hrs due to compressor inlet temperature deviation alarm
144 |  | 17:22 | ST | ST Engaged
145 | 28.03.23 | 8:12 & 8:34 | ST & GT | Shutdown | ST Shutdown at 08:12 hrs and GT at 08:34 hrs due to Air intake filter Replacement. | Coalescer filter change
146 |  | 14:39 | GT | Synchronized
147 |  | 17:28 | ST | ST Engaged
148 | 06.04.23 | 14:03 | GT & ST | Tripped | GT Tripped at 14:03 hrs due to Compressor inlet Temp. deviation alarm.
149 |  | 15:11 | GT | Synchronized
150 |  | 15:42 | GT | Shutdown | GT Shutdown at 15:42 hrs due to Exhaust temp. deviation (cold Spot)
151 |  | 16:57 | GT | Synchronized
152 |  | 18:25 | ST | ST Engaged
153 | 08.04.23 | 14:54 | GT & ST | Tripped | GT Tripped at 14:54 hrs due to GT Compressor Outlet Pressure fall. | CC Inspection (07 pcs tiles changed)
154 | 21.04.23 | 275:46 | GT | Synchronized
155 |  | 20:12 | ST | ST Engaged
156 | 25.04.23 | 313:26 | GT & ST | Tripped | GT Tripped at 13:06 hrs due to ACCL Monitoring > max3. | CC Inspection and air intake cone maintenance (80 pcs tiles changed)
157 | 05.06.23 | 23:33 | GT | Synchronized
158 | 06.06.23 | 22:55 | ST | ST Engaged
159 | 04.07.23 | 15:28 | ST | ST Disengaged | ST given shutdown at 15:28 hrs due to Travelling band screen problem
160 | 07.07.23 | 122:38 | ST | ST Engaged
| 03.08.23 |  |  | Plant Running |  | 03.08.2023 Coalescer filter change on line
161 | 06.09.23 | 14:12 | GT | Tripped | GT Triped at 14:12 hrs due to Turbine outlet temperature protection and MI done. | Combustion chamber inspection by Siemens free of cost there was no tiles and other spare parts needed
162 | 28.09.23 | 9:26 | GT | Synchronized
163 |  | 15:01 | ST | ST Engaged
164 | 06.10.23 | 0:47 | ST | Tripped | ST tripped at 00:47 hrs due to frequency flactuation (Grid problem).
165 |  | 5:44 | ST | ST Engaged
166 | 03.11.23 | 1:01 | GT & ST | Shutdown | ST Dis-engage at 00:53 hrs and GT Shutdown at 01:01 hrs for Air Filter Replacement. | Coalescer and Pre filter change
167 | 06.11.23 | 0:08 | GT | Synchronized
168 |  | 4:38 | ST | ST Engaged
| 24.12.23 | 3.07 | ST | Shutdown | Due to gas shortage. | Fine filter change
|  | 100:05 | GT
| 25.12.23 | 22.17 | GT | GT Engaged
|  | 1.18 | ST | ST Engaged
169 | 01.01.24 | 17:23 | GT & ST | Tripped | Plant tripped at 17:23 hrs due to over frequency (400KV Bus tripped) and GT Accl. Monitoring> Max 3 came. MI done | Performed MI from 2.01.2024 to 10.01.2024 (10 pcs tiles changed)
170 | 10.01.24 | 20:20 | GT | Synchronized
171 | 11.01.24 | 6:59 | GT | Shutdown | For Hot start start checking but failed
172 | 11.01.24 | 8:55 | GT | Synchronized
173 | 11.01.24 | 13:52 | ST | ST Engaged
174 | 18.01.24 | 14:36 | GT & ST | Shutdown | Given shutdown due to gas pressure low as per NLDC Instruction
175 | 15.02.24 | 1:04 | GT | Synchronized
176 |  | 7:36 | ST | ST Engaged
177 | 17.02.24 | 8:38 | GT & ST | Tripped | Main lube oil tank level sensor fault. | Sensor replaced.
178 |  | 17:32 | GT | Synchronized
179 |  | 20:21 | ST | ST Engaged
180 | 29.02.24 | 15:55 | ST | Shutdown | ST given shutdown for HP emergency shut-off valve problem (found nut loose)
181 | 01.03.24 | 6:18 | GT | Shutdown | For Bearing vibration check
182 |  | 11:45 | GT | Synchronized
183 |  | 22:05 | ST | ST Engaged
184 | 07.03.24 | 11:51 | GT & ST | Tripped | Unit Auxiliary transformer protection trip (UAT). Winding temperature relay mulfunction.
185 |  | 15:37 | GT | Synchronized
186 |  | 18:52 | ST | ST Engaged
187 | 15.03.24 | 8:00 | GT | Shutdown | For Intake air filter replacement (Coalessor filter only)
188 | 16.03.24 | 19:42 | GT | Synchronized
189 |  | 21:57 | ST | ST Engaged
190 | 19.07.24 | 19:21 | GT & ST | Tripped | Plant tripped at 19:41 hrs due to GBC-1 tripped and not started due to some schedule work (Off-line wash, Air filter replacement, Lp control valve replacement and IGV cleaning)
191 | 24.07.24 | 12:31 | GT | Synchronized
192 |  | 19:04 | ST | ST Engaged
193 | 10.11.24 | 12:25 | GT & ST | Tripped | GT Triped at 12:25 hrs due to Turbine outlet temperature protection.